4790 W. 73rd Street

Indianapolis, IN 46268

/ 317.290.1900 – F

bmaher@aesrack.com

www.aesrack.com

PRODUCT SPECIFICATION

A 1) ER-130 - ER-130-200/250 or ER-130-215 Air Rotation Units

FAN - (1) 30” 1/2 hp, 115/1 - 12 amps

Rated at 9,000 cfm

Noise level not to exceed 12 sones – 64 dba

Fan blade galvanized G90 steel minimum 16 gauge – epoxy coated

hub - keyed to fan shaft

Unit’s Construction Consists Of:

A fully assembled wall housing constructed of 20 gauge

pre-painted Sierra Color-Klad metal with PVC protective coating

to prevent scratching during installation

Vibration isolators mounted between fan and fan wall housing

Primed and painted 3/16” welded angle iron frame - vibration isolators mounted

between fan wall housing and welded angle iron mounting frame

OSHA approved front guard located between the fan and the discharge blades

OSHA approved back guard located between the fan and the inlet of the fan

4-way 20 gauge 360 degree discharge blades

(7) 32” x 5” front up and down individually pipe locked to reduce blade raw edges

discharge air blades

(14) 12” x 5” side up and down individually pipe locked to reduce blade raw edges

discharge air blades

(6) 34” x 5” internal left and right individually pipe locked to reduce blade raw edges

discharge air blades located on the inside of the fan wall assemble

Fan blades anchored with ¼” nylon inset nut and bolts to eliminate loosening

of the blades during operation

Unit Mounted Control Panel:

Constructed out of Pre-painted color-Klad metal

10” x 16” bolted to wall housing

120/1 service switch mounted on wall housing

Fan’s ¾ hp motor wired from motor to unit mounted service switch

120/1 to 24 volt transformer

15 amp motor fuse for motor over-load protection

Remote Control Panel:

10” x 8” x 4” electrical enclosure

24 volt on/off fan toggle switch with operating with 24 volt operating

light

Toggle switch energizes unit heater – unit heater cannot run with out

Distribution fan running

7 day 24 hour 24 volt programmable thermostat

PAGE TWO

ER-130-200/250 With (1) 200,000 or (1) 250,000 Btu/hr 80% Unit Heater:

ER-130-215 With (1) 215,000 Btu/hr 93% Unit Heater:

Primed and painted 3/16” welded angle iron frame - vibration isolators mounted

between unit heater and welded angle iron mounting frame

(6) ½ “ pre-punched holes for mounting – unit’s hung with 3/8” all-thread rod

Unit heater’s welded mounting frame shipped loose (attached to main unit) –

Both the ER-130 and unit heater frame will have (3) ½” holes punched in frame

Frames bolted together in the field

Bolts supplied by ER mfg

Note - Btu/hr and size of unit may vary depending on the unit heater mfg

ER-130 Cooling Unit:

A fully assembled wall housing constructed of 20 gauge

pre-painted Sierra Color-Klad metal with PVC protective coating

to prevent scratching during installation

Unit Top inlet for supply roof top unit consisting 48” x 20” opening located on the

top of the unit

(1) 36” x 22” back panel to isolate discharge air from roof top unit housing

constructed of 20 gauge pre-painted Sierra Color-Klad metal with PVC protective

coating to prevent scratching during installation

(1) 36” x 14” deflector panel to deflect roof top supply air into ER-142 unit constructed

of 20 gauge pre-painted Sierra Color-Klad metal with PVC protective coating to

prevent scratching during installation

Sue

2011-07-14

Dave Philpott

Microsoft